Procedure for Hot Work at the Zeppelin Observatory

1.0 Purpose

Ensure the safe execution of hot work at the Zeppelin Observatory to prevent fire, as well as damage to health, equipment, and infrastructure. Prevent accidental and unnecessary activation of the integrated automatic fire suppression system.

1.1 Scope

This procedure applies to all personnel who are staying at and/or performing work at the Zeppelin Observatory.

Definition of Hot Work – Hot work includes all tasks involving tools or equipment that generate sparks or heat which may cause fire. This includes, but is not limited to, heat guns, soldering, welding, angle grinders, etc.

Also included: planned release of aerosols/particles for instrument calibration purposes.

1.2 Instructions

All hot work or planned release of aerosols/particles at the Zeppelin Observatory must be approved by one of the engineers.

If the task can be carried out by moving the equipment to the electronics workshop at Sverdrup, this is the preferred option.

Before any hot work or planned release of aerosols/particles can begin, it must be verified that the Safe Job Analysis for Hot Work and Planned Release of Aerosols and Particles at the Zeppelin Observatory has been read and completed.

Prior to starting any hot work or planned release of aerosols/particles, the automatic fire suppression system must be switched to manual mode. The smoke detectors in the zone where work will be conducted must be disabled on the fire alarm panel and physically covered with a red cap to prevent particles from entering the sensor. This task must be performed by operations engineers from the Norwegian Polar Institute.

No hot tools or materials may be placed directly on surfaces without adequate protection for the surroundings.

Approved and appropriate personal protective equipment (PPE) must be used during the work.